## Data
Parameter | Unit | Effluent | RGF | Te (%) | Ozone | Te (%) | GAC | Te (%) | UF | Te (%) | Final | Te (%)
Algal count | cells/mL | 1488 | 129 | 91.3306 | 8 | 93.7984 | 8 | 0 | 0 | 100 | - | -
HPC 37 | cfu/mL | - | 1000.00 | - | 4 | 99.60 | 1000 | - | 1 | 99.90 | 0 | 100
Giardia | Cysts/10L | - | 0 | - | 0 | - | 0 | - | 0 | - | 0 | -
Cl | mg/L | 37.2 | 41.9 | 0 | 40.9 | 2.3866 | 42.5 | 0 | 42.4 | 0.23529 | 48 | 0
Cl2 (F) | mg/L | 0.05 | 0.05 | - | 0.05 | - | 0.05 | - | 0.05 | - | 0.05 | -
Cu | mg/L | 0.05 | 0.05 | - | 0.05 | - | 0.05 | - | 0.05 | - | 0.05 | -
Fe | mg/L | 0.02 | 0.03 | 0 | 0.02 | 33.33 | 0.02 | - | 0.02 | - | 0.02 | -
SS | mg /L | 12 | 10.00 | 16.67 | 10.0 | - | 10.0 | - | 10.0 | - | 10.00 | 16.67
TDS | mg /L | 246 | 262 | 0 | 247 | 5.7252 | 245 | 0.80972 | 243 | 0.81633 | 264 | 0
Mn | mg/L | 0.01 | 0.04 | 0 | 0.04 | 0 | 0.05 | 0 | 0.05 | 0 | 0.05 | 0
NH3 | mg N/L | 0.50 | 10.0 | 80.00 | 0.10 | - | 0.10 | - | 0.10 | - | 0.10 | 80.00
NO2 | mg N/L | 0.50 | 10.0 | 80.00 | 0.10 | - | 0.10 | - | 0.10 | - | 0.10 | 80.00
NO3 | mg N/L | 0.79 | 2.15 | Nil | 2.06 | 4.186 | 2.58 | 0 | 2.58 | 0 | 2.68 | 0
Na | mg/L | 34.9 | 37.5 | Nil | 37.6 | 0 | 37.8 | 0 | 38 | 0 | 42.6 | 0
Colour | mg Pt-Co/L | 7.2 | 7.1 | 1.3889 | 1.00 | 85.92 | 1.00 | - | 1.00 | - | 1.00 | 86.11
SO4 | mg/L | 35.2 | 37.2 | 0 | 37.3 | 0 | 37.1 | 0.53619 | 37.1 | 0 | 37.3 | 0
Zn | mg/L | 0.04 | 0.03 | 25.00 | 0.03 | - | 0.03 | - | 0.03 | - | 0.03 | 25.00
Coliforms | MPN/100mL | 24196 | 201 | 99.17 | 201 | 0 | 201 | 0 | 0 | 100 | 0 | 100
E.coli | MPN/100mL | 7270 | 201 | ~97.24 | 0 | 100 | 66 | 0 | 0 | 0 | 0 | 100
Conductivity | mS/m | 41 | 43.3 |  | 42.9 |  | 43.4 |  | 43.4 |  | 45.7
Combined NO3 + NO2 ratio | - | 0.82 | 0.31 | 62.1951 | 0.3 | 3.2258 | 0.35 | 0 | 0.35 | 0 | 0.35 | 57.3171
Combined THM Ratio | - | 0.40 | 0.40 | - | 0.40 | - | 0.40 | - | 0.42 | - | 0.73 | -
Odour | - | Mild Musty | Nil |  | Nil |  | Nil |  | Nil |  | Mild Chlorinous
pH | - | 7.5 | 7.7 |  | 7.73 |  | 7.46 |  | 7.56 |  | 7.52
Turbidity | NTU | 3.5 | 0.5 | 85.7143 | 0.2 | 60 | 0.2 | 0 | 0.2 | 0 | 0.1 | 97.1429
Cryptosporidium | oocyst/10L | - | 0 | - | 0 | - | 0 | - | 0 | - | 0 | -
Coliphages | PFU/10ml | 84 | 31 | 63.0952 | 0 | 100 | 1 | - | 0 | 100 | 0 | -
Al | µg/L | 29.2 | 27.7 | 5.137 | 28.1 | 0 | 25.00 | 11.08 | 25.0 | - | 25.00 | 14.38
As | µg/L | 2.88 | 3.51 | 0 | 3.78 | 0 | 4.19 | 0 | 4.07 | 2.864 | 4.79 | 0
B | µg/L | 52.3 | 48.4 | 7.457 | 52 | 0 | 52.1 | 0 | 49.9 | 4.2226 | 51.7 | 1.1472
Ba | µg/L | 11.2 | 10.00 | 10.71 | 10.0 | - | 10.0 | - | 10.0 | - | 10.0 | 10.71
Cd | µg/L | 1.00 | 1.00 | - | 1.00 | - | 1.00 | - | 1.00 | - | 1.00 | -
CN (T) | µg/L | 25.0 | 25.0 | - | 25.0 | - | 25.0 | - | 25.0 | - | 25.0 | -
Cr (T) | µg/L | 5.00 | 5.00 | - | 5.00 | - | 5.00 | - | 5.00 | - | 5.00 | -
F | µg/L | 100 | 100 | - | 100 | - | 100 | - | 100 | - | 100 | -
Hg | µg/L | 0.50 | 0.50 | - | 0.50 | - | 0.50 | - | 0.50 | - | 0.50 | -
Phenols | µg/L | 10.0 | 10.0 | - | 10.0 | - | 10.0 | - | 10.0 | - | 10.0 | -
CHCl3 | µg/L | 10 | 10 | - | 10 | - | 10 | - | 16.2 | - | 29.9 | -
CHCl2Br | µg/L | 10 | 10 | - | 10 | - | 10 | - | 10 | - | 20.8 | -
CHClBr2 | µg/L | 10 | 10 | - | 10 | - | 10 | - | 10 | - | 18.1 | -
CHBr3 | µg/L | 10 | 10 | - | 10 | - | 10 | - | 10 | - | 10 | -
Ni | µg/L | 10.0 | 10.0 | - | 10.0 | - | 10.0 | - | 10.0 | - | 10.0 | -
Pb | µg/L | 4.00 | 4.00 | - | 4.00 | - | 4.00 | - | 4.00 | - | 4.00 | -
Sb | µg/L | 2.00 | 2.00 | - | 2.00 | - | 2.00 | - | 2.00 | - | 2.00 | -
Se | µg/L | 2.00 | 2.00 | - | 2.00 | - | 2.00 | - | 2.00 | - | 2.00 | -
U | µg/L | - | 1.00 | - | 1.00 | - | 1.00 | - | 1.00 | - | 1.00 | -

## Sheet4
Parameter | Algal count | HPC 37 | Giardia | Cl | Cl2 (F) | Cu | Fe | SS | TDS | Mn | NH3 | NO2 | NO3 | Na | Colour | SO4 | Zn | Coliforms | E.coli | Conductivity | Combined NO3 + NO2 ratio | Combined THM Ratio | Odour | pH | Turbidity | Cryptosporidium | Coliphages | Al | As | B | Ba | Cd | CN (T) | Cr (T) | F | Hg | Phenols | CHCl3 | CHCl2Br | CHClBr2 | CHBr3 | Ni | Pb | Sb | Se | U
Unit | cells/mL | cfu/mL | Cysts/10L | mg/L | mg/L | mg/L | mg/L | mg /L | mg /L | mg/L | mg N/L | mg N/L | mg N/L | mg/L | mg Pt-Co/L | mg/L | mg/L | MPN/100mL | MPN/100mL | mS/m | - | - | - | - | NTU | oocyst/10L | PFU/10ml | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L | µg/L
Effluent | 1488 | - | - | 37.2 | 0.05 | 0.05 | 0.02 | 12 | 246 | 0.01 | 0.50 | 0.50 | 0.79 | 34.9 | 7.2 | 35.2 | 0.04 | 24196 | 7270 | 41 | 0.82 | 0.40 | Mild Musty | 7.5 | 3.5 | - | 84 | 29.2 | 2.88 | 52.3 | 11.2 | 1.00 | 25.0 | 5.00 | 100 | 0.50 | 10.0 | 10 | 10 | 10 | 10 | 10.0 | 4.00 | 2.00 | 2.00 | -
RGF | 129 | 1000.00 | 0 | 41.9 | 0.05 | 0.05 | 0.03 | 10.00 | 262 | 0.04 | 10.0 | 10.0 | 2.15 | 37.5 | 7.1 | 37.2 | 0.03 | 201 | 201 | 43.3 | 0.31 | 0.40 | Nil | 7.7 | 0.5 | 0 | 31 | 27.7 | 3.51 | 48.4 | 10.00 | 1.00 | 25.0 | 5.00 | 100 | 0.50 | 10.0 | 10 | 10 | 10 | 10 | 10.0 | 4.00 | 2.00 | 2.00 | 1.00
Te (%) | 91.3306 | - | - | 0 | - | - | 0 | 16.67 | 0 | 0 | 80.00 | 80.00 | Nil | Nil | 1.3889 | 0 | 25.00 | 99.17 | ~97.24 |  | 62.1951 | - |  |  | 85.7143 | - | 63.0952 | 5.137 | 0 | 7.457 | 10.71 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Ozone | 8 | 4 | 0 | 40.9 | 0.05 | 0.05 | 0.02 | 10.0 | 247 | 0.04 | 0.10 | 0.10 | 2.06 | 37.6 | 1.00 | 37.3 | 0.03 | 201 | 0 | 42.9 | 0.3 | 0.40 | Nil | 7.73 | 0.2 | 0 | 0 | 28.1 | 3.78 | 52 | 10.0 | 1.00 | 25.0 | 5.00 | 100 | 0.50 | 10.0 | 10 | 10 | 10 | 10 | 10.0 | 4.00 | 2.00 | 2.00 | 1.00
Te (%) | 93.7984 | 99.60 | - | 2.3866 | - | - | 33.33 | - | 5.7252 | 0 | - | - | 4.186 | 0 | 85.92 | 0 | - | 0 | 100 |  | 3.2258 | - |  |  | 60 | - | 100 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GAC | 8 | 1000 | 0 | 42.5 | 0.05 | 0.05 | 0.02 | 10.0 | 245 | 0.05 | 0.10 | 0.10 | 2.58 | 37.8 | 1.00 | 37.1 | 0.03 | 201 | 66 | 43.4 | 0.35 | 0.40 | Nil | 7.46 | 0.2 | 0 | 1 | 25.00 | 4.19 | 52.1 | 10.0 | 1.00 | 25.0 | 5.00 | 100 | 0.50 | 10.0 | 10 | 10 | 10 | 10 | 10.0 | 4.00 | 2.00 | 2.00 | 1.00
Te (%) | 0 | - | - | 0 | - | - | - | - | 0.80972 | 0 | - | - | 0 | 0 | - | 0.53619 | - | 0 | 0 |  | 0 | - |  |  | 0 | - | - | 11.08 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
UF | 0 | 1 | 0 | 42.4 | 0.05 | 0.05 | 0.02 | 10.0 | 243 | 0.05 | 0.10 | 0.10 | 2.58 | 38 | 1.00 | 37.1 | 0.03 | 0 | 0 | 43.4 | 0.35 | 0.42 | Nil | 7.56 | 0.2 | 0 | 0 | 25.0 | 4.07 | 49.9 | 10.0 | 1.00 | 25.0 | 5.00 | 100 | 0.50 | 10.0 | 16.2 | 10 | 10 | 10 | 10.0 | 4.00 | 2.00 | 2.00 | 1.00
Te (%) | 100 | 99.90 | - | 0.23529 | - | - | - | - | 0.81633 | 0 | - | - | 0 | 0 | - | 0 | - | 100 | 0 |  | 0 | - |  |  | 0 | - | 100 | - | 2.864 | 4.2226 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Final | - | 0 | 0 | 48 | 0.05 | 0.05 | 0.02 | 10.00 | 264 | 0.05 | 0.10 | 0.10 | 2.68 | 42.6 | 1.00 | 37.3 | 0.03 | 0 | 0 | 45.7 | 0.35 | 0.73 | Mild Chlorinous | 7.52 | 0.1 | 0 | 0 | 25.00 | 4.79 | 51.7 | 10.0 | 1.00 | 25.0 | 5.00 | 100 | 0.50 | 10.0 | 29.9 | 20.8 | 18.1 | 10 | 10.0 | 4.00 | 2.00 | 2.00 | 1.00
Te (%) | - | 100 | - | 0 | - | - | - | 16.67 | 0 | 0 | 80.00 | 80.00 | 0 | 0 | 86.11 | 0 | 25.00 | 100 | 100 |  | 57.3171 | - |  |  | 97.1429 | - | - | 14.38 | 0 | 1.1472 | 10.71 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## one line description
One-line Description of the Data:
This dataset records water quality parameters and removal efficiencies (Te %) at different stages of a wastewater treatment process to evaluate treatment performance

## data dictionaryvariable_name de
variable_name | description
Algal count | The concentration of algae in water measured in cells per milliliter.
HPC 37 | Heterotrophic Plate Count at 37°C, an indicator of bacterial growth.
Giardia | Cysts of Giardia species present in water.
Cl | Concentration of chloride ions measured in milligrams per liter.
Cl2 (F) | Concentration of free chlorine in water.
Cu | Concentration of copper ions measured in milligrams per liter.
Fe | Concentration of iron ions measured in milligrams per liter.
SS | Suspended solids in water measured in milligrams per liter.
TDS | Total dissolved solids in water measured in milligrams per liter.
Mn | Concentration of manganese ions measured in milligrams per liter.
NH3 | Concentration of ammonia in water measured in milligrams of nitrogen per liter.
NO2 | Concentration of nitrite in water measured in milligrams of nitrogen per liter.
NO3 | Concentration of nitrate in water measured in milligrams of nitrogen per liter.
Na | Concentration of sodium ions measured in milligrams per liter.
Colour | Measurement of water color in milligrams of platinum-cobalt per liter.
SO4 | Concentration of sulfate ions measured in milligrams per liter.
Zn | Concentration of zinc ions measured in milligrams per liter.
Coliforms | Coliform bacteria count in water measured in MPN per 100 milliliters.
E.coli | E. coli bacteria count in water measured in MPN per 100 milliliters.
Conductivity | Ability of water to conduct electricity, measured in milliSiemens per meter.
Unit | Measurement unit for the parameter.
Effluent | Concentration or value measured in the effluent stream.
RGF | Concentration or value measured after Rapid Gravity Filter (RGF).
Te (%) | Removal efficiency achieved at the RGF stage.
Ozone | Concentration or value after ozone treatment.
Te (%) | Removal efficiency achieved during ozone treatment.
GAC | Granular Activated Carbon (GAC) treatment.
Te (%) | Removal efficiency achieved during GAC treatment.
UF | Concentration or value after Ultrafiltration (UF) treatment.
Te (%) | Removal efficiency achieved during UF treatment.
Final | Final concentration or value after all treatment stages.
Te (%) | Overall removal efficiency across all stages.

## description
One-paragraph Description of the Data:
This dataset contains water quality parameters measured at various stages of a wastewater treatment process, including Effluent, RGF, Ozone, GAC, UF, and Final treated water. It records measurements of chemical, physical, and biological parameters, such as pH, turbidity, nutrient levels, and microbial contaminants, along with percentage removal efficiencies (Te %). The data was collected to evaluate the treatment plant's performance and compliance with effluent discharge standards.